{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Table 1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Table 1","index":0,"n_rows":187,"n_cols":9,"rows_kept":187,"cut":false,"hidden":false,"merged":[[0,0,0,7],[0,8,2,8],[3,0,3,7],[94,0,94,7],[137,0,137,7],[107,0,108,0],[1,1,2,1],[1,2,2,2],[12,1,13,1],[12,2,13,2],[114,0,116,0],[1,4,2,4],[100,0,101,0],[56,0,93,0],[112,0,113,0],[103,0,105,0],[179,0,179,7],[148,3,148,7],[161,3,161,7],[188,0,188,8],[187,0,187,8],[186,0,186,8],[172,0,172,7],[173,0,173,7],[174,0,174,7],[175,0,175,7],[178,0,178,7],[185,0,185,8],[181,0,181,7],[180,0,180,7],[149,3,149,7],[177,0,177,7],[37,0,55,0],[95,0,99,0],[4,0,36,0],[1,5,1,7],[1,0,2,0],[12,3,13,3],[12,4,13,4],[1,3,2,3],[133,0,135,0],[148,0,162,0],[110,0,111,0],[184,0,184,8],[138,0,147,0],[183,0,183,8],[182,0,182,8],[118,0,120,0],[121,0,128,0],[121,8,125,8],[129,0,130,0],[163,3,163,7],[143,3,143,7],[144,3,144,7],[163,0,171,0],[176,0,176,7]]}
["TABLE 1 – Monitoring Points, Alarm & Trend Requirements (Mechanical Equipment)",{"$nulls":7},"Notes to Editor"]
["System","Point","Point Type","Trend (6)","Setpoint (1)","Alarm (4, 5)"]
[{"$nulls":5},"Description (3)","Alarm Delay","Priority (2)"]
["Central Plant Equipment"]
["Air Handling Units","Supply Fan motor Start/Stop","DO","X",null,"No Alarm Required"]
[null,"Supply Fan Status","DI","X",null,"If status does not match start/stop command","60 sec","high- critical, med-noncritical","For VFD fans, use contact on VFD.  For non-VFD fan, use a current sensing relay.  Review with project engineer."]
[null,"Supply Fan Isolation Damper","DI","X",null,"If damper position does not match command","30 sec","high- critical, med-noncritical","Isolation damper shall be hardwired to fan starter/ VFD and provided with an endswitch"]
[null,"Supply Fan VFD Speed","AO","X",null,"No Alarm Required"]
[null,"Return Fan motor Start/Stop","N/A","X",null,"No Alarm Required",null,null,"Return fan to be hard-wire interlocked with supply fan."]
[null,"Return Fan Status","DI","X",null,"If status does not match start/stop command","60 sec","high- critical, med-noncritical","For VFD fans, use contact on VFD.  For non-VFD fan, use a current sensing relay.  Review with project engineer."]
[null,"Return Fan Isolation Damper","DI","X",null,"If damper position does not match command","30 sec","high- critical, med-noncritical","Isolation damper shall be hardwired to fan starter/ VFD and provided with an endswitch"]
[null,"Return Fan VFD Speed","AO","X",null,"No Alarm Required"]
[null,"Discharge Air Temperature","AI","X","i.e. 55°F","If DAT is > +/-2°F of set point for critical, > +/-5°F of set point for noncritical",null,"med","Shall be installed down stream of supply fan & humidifier to read actual temperature supplied to terminal equipment."]
[{"$nulls":5},"If DAT is less than 10°F PAT when the chilled water valve is commanded closed.","15 min","med"]
[null,"Discharge Air humidity","AI","X","i.e. 90%RH","If humidification is enabled and DAH > 90% relative humidity","2 min","high","Only on systems including humidifiers."]
[null,"Supply Air Distribution Duct Static Pressure","AI","X","i.e. 1.5\" WC","If > +/-0.5\"WC of set point",null,"med","Typical each transmitter"]
[null,"Return Air Distribution Duct Static Pressure","AI","X","i.e. -1.5\" WC","If > +/-0.5\"WC of set point",null,"med","Typical each transmitter"]
[null,"Supply Fan High Static Pressure Limit","DI",null,"i.e. 5.5\"WC","High Static Pressure Shutdown",null,"high","Mounted at the supply discharge of the Air handling Unit.  "]
[null,"Return Fan Low Static Pressure Limit","DI",null,"ie -5.5\"WC","Low Static Pressure Shutdown",null,"high","Mounted at the return inlet of the Return Fan. "]
[null,"Humidifier Control Valve","AO","X",null,"No Alarm Required",null,null,"Only on systems including humidifiers."]
[null,"Cooling Coil Control Valve","AO","X",null,"No Alarm Required"]
[null,"Preheat Coil Control Valve","AO","X",null,"No Alarm Required"]
[null,"Preheat Coil Pump Start/Stop","DO",null,null,"No Alarm Required",null,null,"Preheat coil recirculation pump"]
[null,"Preheat Coil Pump Status","DI",null,null,"If status does not match start/stop command","60 sec","med","Shall be monitored by a current sensing relay."]
[null,"Freeze stat ","DI","X","i.e. 36°F","When freeze stat is activated","None","high","Freeze stat shall be installed upstream of cooling coil.  Freeze stat alarm shall shut-down AHU."]
[null,"Preheat Air Temperature","AI","X","i.e. 50°F","If PAT is more than 10°F > mixed air temperature when the preheat valve is commanded closed.","15 min","med","Mounted downstream of preheat coil and upstream of freeze stat."]
[null,"Mixed Air Temperature","AI","X",null,"No Alarm Required"]
[null,"Mixed Air Dampers","AO","X",null,"No Alarm Required"]
[null,"Return Air Temperature","AI","X",null,"No Alarm Required",null,null,"Mounted upstream of return fan."]
[null,"Return Air Humidity","AI","X","i.e. 60%RH high/ 30% RH low","If humidity is <27% RH or >63% RH ",">6 hrs continuously","med  >6hrs, high >12 hrs","Mounted upstream of return fan.  Low humidity alarm only applicable in facilities required to maintain 30%RH min."]
[null,"Return Air Enthalpy","AI or Virtual",null,null,"No Alarm Required",null,null,"Preferred method is to calculate enthalpy based on dry bulb temperature and relative humidity sensor inputs."]
[null,"AHU SA Smoke Damper","DI","X",null,"If damper position does not match command","90 sec","high","Trend only required on critical AHU's"]
[null,"AHU RA Smoke Damper","DI","X",null,"If damper position does not match command","90 sec","high","Trend only required on critical AHU's"]
[null,"Fire Alarm Shutdown","DI","X",null,"Fire Alarm shutdown","None","life","Trend only required on critical AHU's"]
[null,"Supply Airflow","AI","X",null,"No Alarm Required"]
[null,"Return Airflow","AI","X",null,"No Alarm Required"]
[null,"Outside Airflow","AI","X","i.e. xxxx CFM","If system outside air CFM is > 10% below setpoint for min OA","5 min","med","Only applies to specific system types.  Can be accomplished via direct outside airflow measurement or calculated between multiple airflow sensors.  Consult with project engineer."]
["Heating Hot Water/ Boiler Plant","Boiler Enable/ Disable","DO",null,null,"No Alarm Required"]
[null,"Boiler Temperature Set point","AO",null,"i.e. 130°F","No Alarm Required",null,null,"Hardwired I/O or integrated "]
[null,"Boiler Alarm","DI",null,null,"General Alarm","None","high","General alarm from boiler control panel."]
[null,"Boiler Status","DI","X",null,"Alarm if boiler is enabled and fail to prove status","60 sec","high"]
[null,"HHW Set point","AO","X","i.e. 130°F","No Alarm Required"]
[null,"Boiler/HX Supply Temp Sensor","AI","X",null,"Alarm if > +/-10°F of set point or if > 220 degF","5 min","high","Include at the output of each boiler or heat exchanger in the system."]
[null,"Boiler/HX Isolation Valve Position","DO",null,null,"No Alarm Required"]
[null,"Boiler/HX Isolation Valve Position","DI",null,null,"If position does not match DO command","60 sec","high","Via valve end switch."]
[null,"Loop Supply Temperature","AI","X","i.e. 130°F","Alarm if > +/-10°F of set point","5 min","high","Each primary, secondary, tertiary, etc. loop should have a supply temperature sensor."]
[null,"Loop Return Temperature","AI","X",null,"No Alarm Required",null,null,"Each primary, secondary, tertiary, etc. loop should have a return temperature sensor."]
[null,"Loop Flow","AI","X",null,"No Alarm Required",null,null,"Each primary, secondary, tertiary, etc. loop should have a GPM flow meter or a means of calculating loop flow from other system flowmeters."]
[null,"Heating Energy Load","Virtual AI","X",null,"No Alarm Required",null,null,"System shall utilize supply and return temperature sensors and flow meters to calculate the system energy load, displayed as MBtu/hr."]
[null,"HHW Makeup Water Flow","DI","X",null,"Alarm if > 5 GPM","2 min","med"]
[null,"Differential Pressure","AI","X","i.e. 15 psi","Alarm if > +/- 20% of set point","2 min","med","Differential pressure sensor comparing supply & return pressures.  Consult with the project engineer for quantity and relevant locations."]
[null,"HHW System Pressure","AI",null,null,"Alarm if > 10 psig below fill pressure","5 min","high","Mounted at makeup water connection"]
[null,"HX Steam Control Valve","AO",null,null,"No Alarm Required",null,null,"Only applies to systems with heat exchangers.  Individual outputs to the steam control valve serving each heat exchanger."]
[null,"Pump Start/Stop","DO",null,null,"No Alarm Required"]
[null,"Pump Status","DI","X",null,"If status does not match start/stop command","60 sec","high","Shall be monitored by a current sensing relay or a contact on the fan VFD.  Review with project engineer."]
[null,"Pump VFD Speed","AO","X",null,"No Alarm Required"]
["Chilled Water Plant","Chiller Enable","DO",null,null,"No Alarm Required"]
[null,"CHW Set point","Integrated AO","X","i.e. 42°F","Alarm if > +/-4°F of set point","10 min","high"]
[null,"Chiller Alarm","DI",null,null,"General Alarm","None","high","General Alarm from chiller control panel."]
[null,"Chiller Status","DI","X",null,"Alarm if chiller is enabled and failed to prove status","90 sec","high"]
[null,"Chiller Refrigerant Relief Valve Status","DI",null,null,"If relief valve opens","None","life"]
[null,"Chiller %RLA","Integrated AI","X",null,"No Alarm Required",null,null,"Integrate from the chiller control panel."]
[null,"Chiller KW","Integrated AI","X",null,"No Alarm Required",null,null,"Integrate from the chiller control panel."]
[null,"Chiller Isolation Valve","DO",null,null,"No Alarm Required"]
[null,"Chiller Isolation Valve Position","DI",null,null,"If position does not match DO command","60 sec","high","From valve end switch."]
[null,"Primary Pump Status","DI","X",null,"If status does not match start/stop command","60 sec","high","Preferred control is for the chiller control panel to command primary pumps on and off.  DI point shall report pump status to BMS.  Applies to primary CHW and CW pumps."]
[null,"Chiller/HX CHW Supply Temperature","AI","X",null,"No Alarm Required",null,null,"Temperature sensor at the chilled water outlet of each chiller or heat exchanger as applicable."]
[null,"Chiller/HX CW Return Temperature","AI","X",null,"No Alarm Required",null,null,"Temperature sensor at the condenser water outlet of each chiller or heat exchanger as applicable."]
[null,"CHW Distribution Loop Supply Temperature","AI","X","i.e. 42°F","If temperature is > +/-4°F of set point","10 min","high","Each primary, secondary, tertiary, etc. loop should have a supply temperature sensor."]
[null,"CHW Distribution Loop Return Temperature","AI","X",null,"No Alarm Required",null,null,"Each primary, secondary, tertiary, etc. loop should have a Return temperature sensor."]
[null,"CHW System Pressure","AI","X",null,"Alarm if > 10 psig below fill pressure","5 min","high","Mounted at makeup water connection"]
[null,"CHW Loop Flow","AI","X",null,"If primary loop GPM is <10% above published min flow to maintain chillers.","5 min","med"]
[null,"CHW Makeup Water Flow","DI","X",null,"Alarm if > 5 GPM","2 min","med"]
[null,"Cooling Energy Load","Virtual AI","X",null,"No Alarm Required",null,null,"System shall utilize supply and return temperature sensors and flow meters to calculate the primary loop energy load, displayed as Tons."]
[null,"Total Chiller Electrical Load","Virtual AI","X",null,"No Alarm Required",null,null,"System shall sum active chiller KW and display total chiller KW."]
[null,"Total Plant KW/Ton","Virtual AI","X",null,"No Alarm Required",null,null,"System shall divide total chiller KW by total primary CHW tons to calculate and display total plant chiller KW/Ton."]
[null,"Cond Water Loop Supply Temperature","AI","X",null,"If temperature is > 85°F ",null,"high","For systems with a cooling tower bypass, located upstream of bypass."]
[null,"Cond Water Loop Bypass Temperature","AI","X","i.e. 55°F- 85°F","If temperature is > +/-10°F of set point","5 min","high","For systems with a cooling tower bypass, located downstream of bypass."]
[null,"CW Loop Return Temperature","AI","X",null,"No Alarm Required",null,null,"If the system includes a cooling tower bypass, include a sensor for the chiller side and the tower side of the loop."]
[null,"Cooling Tower Bypass Valve","AO","X",null,"No Alarm Required",null,null,"Only applies to systems with cooling tower bypass valves."]
[null,"Cooling Tower Isolation Valve","DO",null,null,"No Alarm Required"]
[null,"Cooling Tower Isolation Valve Position","DI","X",null,"If position does not match DO command","60 sec","high","From valve end switch."]
[null,"Cooling Tower Vibration","DI","X",null,"If vibration switch is activated",null,"high"]
[null,"Cooling Tower Fan Start/Stop","DO",null,null,"No Alarm Required"]
[null,"Cooling Tower Fan Status","DI","X",null,"If status does not match start/stop command","60 sec","high","Shall be monitored by a current sensing relay or a contact on the fan VFD.  Review with project engineer."]
[null,"Cooling Tower VFD Speed","AO","X",null,"No Alarm Required"]
[null,"Cooling Tower Basin Temperature","AI","X",null,"If temperature below 34°F","5 min","high","Only applies to towers with outdoor basins."]
[null,"Cooling Tower Basin Heater","DO/AO",null,null,"Fault Alarm (if packaged electric heater)",null,"high","Only applies to towers with outdoor basins.  DO or AO for on/off or modulating heating control.  Review with project engineer."]
[null,"Cooling Tower High Level Alarm (Overflow)","DI","X",null,"Overflow Alarm",null,"high"]
[null,"Secondary CHW Pump Start/Stop","DO",null,null,"No Alarm Required"]
[null,"Secondary CHW Pump Status","DI","X",null,"If status does not match start/stop command","60 sec","high","Shall be monitored by a current sensing relay or a contact on the fan VFD.  Review with project engineer."]
[null,"Secondary HHW Pump VFD Speed","AO","X",null,"No Alarm Required"]
[null,"CHW Differential Pressure","AI","X","i.e. 7-15 psi","Alarm if > +/- 20% of set point","2 min","high","Differential pressure sensor comparing supply & return pressures.  Consult with the project engineer for quantity and relevant locations."]
[null,"Chemical Treatment Alarm","DI","X",null,"General Alarm",null,"med"]
["Misc. Mechanical Equipment"]
["Exhaust/ Supply Fans","Fan Enable","DO",null,null,"No Alarm Required"]
[null,"Status","DI","X",null,"If status does not match start/stop command","60 sec","high","For VFD fans, use contact on VFD.  For non-VFD fan, use a current sensing relay.  Review with project engineer."]
[null,"Fan Isolation Damper","DI",null,null,"If damper position does not match command","30 sec","high","Isolation damper shall be hardwired to fan starter/ VFD and provided with an endswitch"]
[null,"Distribution Duct Static Pressure","AI","X","i.e. +/-1.5\" WC","If > +/-0.5\"WC of set point",null,"high","Typical each transmitter"]
[null,"Fan High/ Low Static Pressure Limit","DI",null,"ie +/-5.0\"WC","High/ Low Static Pressure Shutdown",null,"high","If Applicable.  Mounted at the inlet of the Exhaust Fan or discharge of Supply Fan"]
["Sanitary & Storm Pumps","Pump Controller Alarm","DI",null,null,"General Alarm",null,"high","General Alarm from control panel"]
[null,"High Water Alarm","DI",null,null,"High water Alarm",null,"high","Alarm from control panel"]
["Environmental (Hot/ Cold) Rooms","Alarm","DI",null,null,"General Alarm",null,"high","General Alarm from control panel"]
["Heat Trace","Alarm","DI",null,null,"General Alarm",null,"high","Alarm from control panel"]
[null,"OA Temperature - Turn On","AO",null,"i.e. 32°F","No Alarm Required",null,null,"Integrated from control panel"]
[null,"OA Temperature - Turn Off","AO",null,"i.e. 42°F","No Alarm Required",null,null,"Integrated from control panel"]
["RO/ DI Systems","Alarm","DI",null,null,"General Alarm",null,"high","General Alarm from control panel"]
["Glycol make-up Systems","Low Pressure Alarm","DI",null,null,"Alarm",null,"high","Alarm from control panel"]
[null,"Low Level Alarm","DI",null,null,"Alarm",null,"high","Alarm from control panel"]
["Refrigerant Leak Detection","(3) Alarms","DI",null,null,"Detector Fault Alarm, Low Level Refrigerant Leak, TLV/ TWA Alarm",null,"life","From leak detection panel"]
["Booster Pumps","Alarm","DI",null,null,"General Alarm",null,"high","General Alarm from control panel"]
[null,"Discharge Pressure","AI","X","i.e. 90 psi","Alarm if > 10 psig below setpoint",null,"high","Via pressure sensor in downstream piping"]
["Air Compressors","Alarm","DI",null,null,"General Alarm",null,"high","General Alarm from control panel"]
[null,"Discharge Pressure","AI","X","i.e. 100 psi","Alarm if > 10 psig below setpoint",null,"high","Via pressure sensor in downstream piping"]
["Domestic Hot Water Heaters","Discharge Temperature","AI","X","i.e. 120°F","Alarm when HW Temperature is >135°F or < 105°F","5 min","high","Via temperature sensor in downstream piping"]
[null,"Campus HW Temperature","AI","X",null,"Alarm when temperature < 105°F","5 min","high","For facilities supplied by campus tunnel HW service"]
[null,"System Pressure","AI",null,null,"No Alarm Required"]
["Medical Gas Master Alarm System","All points per NFPA 99",null,"X",null,"General Alarm",null,"life","Alarm points from master medical gas alarm panel"]
["Snow melt Systems","Alarm","DI",null,null,"General Alarm","None","med","General Alarm from control panel, if applicable"]
[null,"Glycol temperature","AI",null,"i.e. 130°F","Alarm if > +/-5°F of set point","5 min","med"]
[null,"System Pressure","AI",null,"i.e. 20 psi","Alarm if > 10 psig below fill pressure","5 min","high"]
["Fuel Oil System","Day Tank High Level","DI",null,null,"Alarm","None","life","Typical each Day Tank"]
[null,"Day Tank LowLevel","DI",null,null,"Alarm","None","life"]
[null,"Day Tank Fill Control ","DI",null,null,"Alarm if not in auto","None","life"]
[null,"Day Tank Rupture","DI",null,null,"Alarm","None","life"]
[null,"Day Tank Overflow ","DI",null,null,"Alarm","None","life"]
[null,"Leak Detection Panel","DI",null,null,"Alarm","None","life"]
[null,"Fuel Oil Distribution Pressure","AI ",null,"i.e. 30 psi","Alarm if > 10 psig below setpoint","5 min","life","Alarm inhibited when pumps are not running"]
[null,"Fusible Link Valve Closed ","DI",null,null,"Alarm","None","life"]
["Generator","Generator Trouble","DI",null,null,"Alarm","None","life"]
[null,"Generator Status","DI",null,null,"Generator Running","None","life"]
["Lighting Control","Enable/ Disable","DO",null,null,"No Alarm Required"]
["Water Leak Detection","Alarm","DI",null,null,"General Alarm",null,"life","General Alarm from leak detection panel"]
["UPS (DDC Controller)","Alarm","Integrated DI",null,null,"General Alarm",null,"high"]
[null,"Power Failure/ On Battery","Integrated DI",null,null,"Alarm",null,"high"]
[null,"Output Load","Integrated AI","X",null,"No Alarm Required"]
["DDC Panel Communication","Alarm","DI","X",null,"Alarm",null,"high","Alarm shall be continuous until communication is resumed."]
["Terminal/ Unitary Mechanical Equipment"]
["Computer Room AC Units (CRAC)","CRAC Enable/ Disable","DO"]
[null,"CRAC Status","DI","X",null,"If status does not match start/stop command","60 sec","high","Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"CRAC Alarm","DI",null,null,"General Alarm",null,"high","General Alarm from CRAC unit, if available.  "]
[null,"Fan Status","DI","X",null,"If status does not match start/stop command","60 sec","high","Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Fan Speed","AO",{"$nulls":5},"If applicable"]
[null,"Space/ Return Air Temperature","AI","See Table 2 for Alarm & Trend requirements",{"$nulls":4},"Provide dedicated DDC sensor to monitor temperature, in addition to sensor provided with CRAC unit.  Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Space/ Return Air Humidity","AI","See Table 2 for Alarm & Trend requirements",{"$nulls":4},"Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Discharge Air Temperature","AI","X",null,"If DAT is > +/-2°F of set point",null,"med","Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Cooling Coil Control Valve","AO","X",{"$nulls":4},"Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Smoke Detector Shutdown","DI",null,null,"Smoke Detector shutdown",null,"life","If applicable"]
["VAV/ CAV Box","Thermostat","(2) AI’s ","See Table 2 for Alarm & Trend requirements",{"$nulls":4},"Includes active space temperature and thermostat temperature set point.  Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Airflow","AI ","See Table 2 for Alarm & Trend requirements",{"$nulls":4},"Active VAV box airflow. Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Reheat Valve","Output ",{"$nulls":5},"Output to reheat coil control valve (0 to 100% open)"]
[null,"Damper","Output",{"$nulls":5},"Output to airflow control damper (0 to 100% open)"]
[null,"Heating/ Cooling Mode","DI"]
[null,"Active Temperature Set point","Virtual ",{"$nulls":5},"Active control temperature set point or set points of a control range."]
[null,"Active Airflow Set point","Virtual "]
[null,"Min CFM Set point","Virtual ",{"$nulls":5},"Typical for heating & cooling"]
[null,"Max CFM Set point","Virtual",{"$nulls":5},"Typical for heating & cooling"]
[null,"Discharge Temperature","AI ","X",{"$nulls":4},"Via temperature sensor mounted at discharge of RHC.   Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Perimeter Valve","Output",{"$nulls":5},"Only applies to spaces where a perimeter heater is intended for control by the VAV box controller"]
[null,"Duct Pressure Switch","DI",{"$nulls":5},"Only applies to UH VAV's.  \"No pressure\" status triggers VAV dampers open for smoke control.  Provide override to NORMAL or SMOKE MODE"]
[null,"Occupancy Status","DI",{"$nulls":5},"Only applies to rooms with connected occupancy sensors"]
[null,"Humidity","AI","See Table 2 for Alarm & Trend requirements",{"$nulls":4},"Only applies to rooms with space humidity sensors.   Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Carbon Dioxide","AI",{"$nulls":5},"Only applies to rooms with space carbon dioxide sensors"]
["Fan Coil Unit/ Blower Coil Unit (FCU/ BCU)","Thermostat","(2) AI’s","See Table 2 for Alarm & Trend requirements",{"$nulls":4},"Includes active space temperature and thermostat temperature set point.  Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Active temperature Set points","Virtual",{"$nulls":5},"Active control temperature set point or set points of a control range."]
[null,"Fan Command","DO",{"$nulls":5},"On/off signal to fan motor "]
[null,"Fan Status","DI","X",null,"If status does not match start/stop command","60 sec","high","Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Fan Speed","AO",{"$nulls":5},"Variable speed signal only applies to units with ECM motors."]
[null,"Coil Control Valve","Output",{"$nulls":5},"Output to coil control valve (heating and/or cooling with separate points for each as applicable) (0 to 100% open)"]
[null,"Discharge Temperature","AI ","X",{"$nulls":4},"Via temperature sensor mounted at discharge of FCU/ BCU.   Alarm and trends are only required on units serving critical room types listed in Table 2"]
[null,"Drain Pan Leak Status","DI",null,"N/A","Alarm if leak is detected",null,"high","Via leak detector at cooling coil drain pan"]
[null,"Smoke Detector Shutdown","DI",null,null,"Smoke Detector shutdown",null,"life","If applicable"]
["NOTES:"]
["1. Setpoints are project specific, AE of record to edit setpoints in italics to reflect design"]
["2. Alarm Types: life = Life Safety (0-31 Alarm Priority). high = High Priority (64-95 Alarm Priority). med = Medium Priority (96-127 Alarm Priority). low = Low Priority (128-191 Alarm Priority)"]
["3. All alarm values shall be adjustable thru the frontend graphic"]
["4. Trend Types: COV= Change of Value.   INT= Interval (Interval trends set to time)"]
["4. Configure alarms as indicated.  Alarms in the local DDC shall be configured by the MSCC (Mech System Controls Contractor).  Alarms in the Desigo frontend shall be configured by the SI (Systems Integrator).  "]
["4. MSCC shall configure alarms as indicated. in the local DDC panel.  "]
["5. Alarm requirements based on compliance with ASHRAE 170, 2017 & USP 795/ 797/ 800/ 825"]
["6. Trends shall be configured in the local DDC panel by the MSCC."]
["7.  MM's Desigo front-end operates on (3) servers.  System 1 (instance #9997) encompasses the C&W facility.  System #2 (instance #9998) encompasses Power Monitoring and Area 5 (offsite) buildings.  System 3 (instance #9996) encompasses all remaining facilities on the hill campus (UH, UHS, CVC, CC, THC)."]
[]
["NOTES TO EDITOR:"]
["A. Table is meant to reflect the MINIMUM standardized points, alarms and trends reporting back to UMH’s BMS.  Since control strategies and controller technologies vary greatly form project to project, UMH recognizes that different point and/ or alarm/ trend requirements may be necessary.  Consult with the appropriate UMH FPD Mechanical Engineer."]
["B. See Table 2 for trend/ alarm requirements in critical room applications (ie OR's, Procedure Room, CSPD, Isolation Rooms, Protective Enviro Rooms, Pharmacies, etc), required to ensure compliance.  For room applications not listed in Table 2, generally trend and alarms are not required.  A/E shall exercise judgement on requiring alarms/ trends in non-compliance applications where there is significant risk/ financial implications with HVAC failures (ie consider temperature/ humidity alarming/ trending in medical equipment applications to ensure environmental requirements of the equipment are being met)."]
["C. Alarms should be configured in the local DDC panel for points that are rarely changed by Systems Monitoring.  Alarms should be configured in the Desigo BMS for points that are frequently overridden for operational reasons.  AE shall review alarm configuration requirements with FPD engineer. \t\t\t\t\t\t\t\t\t\t"]