{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Table 2"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Table 2","index":0,"n_rows":143,"n_cols":13,"rows_kept":143,"cut":false,"hidden":false,"merged":[[42,12,45,12],[32,8,33,8],[32,7,33,7],[141,0,141,11],[138,0,138,11],[139,0,139,11],[140,0,140,11],[118,4,119,4],[118,1,119,1],[118,0,120,0],[123,0,126,0],[121,0,122,0],[136,0,136,10],[133,0,133,10],[134,0,134,10],[129,0,129,10],[135,0,135,10],[137,0,137,10],[68,11,69,11],[5,0,8,0],[16,0,19,0],[25,0,27,0],[32,4,33,4],[32,9,33,9],[110,0,112,0],[113,0,115,0],[68,0,69,0],[32,1,33,1],[54,0,57,0],[87,0,89,0],[30,0,33,0],[58,0,61,0],[1,4,2,4],[1,5,1,10],[3,0,4,0],[3,11,4,11],[13,0,15,0],[9,0,12,0],[1,1,2,1],[1,2,2,2],[1,0,2,0],[50,0,53,0],[62,0,65,0],[20,0,22,0],[42,0,45,0],[82,0,84,0],[37,0,39,0],[66,0,67,0],[40,0,41,0],[46,0,49,0],[76,0,79,0],[73,0,75,0],[142,0,142,11],[0,0,0,10],[0,11,2,11],[127,0,127,10],[128,0,128,10],[130,0,130,10],[131,0,131,10],[118,2,119,2],[118,3,119,3],[23,0,24,0],[28,0,29,0],[32,10,33,10],[116,0,117,0],[85,0,86,0],[70,0,72,0],[32,2,33,2],[132,0,132,10],[0,12,2,12],[66,12,67,12],[80,0,81,0],[107,0,109,0],[99,0,100,0],[101,0,103,0],[90,0,92,0],[93,0,95,0],[96,0,98,0],[1,3,2,3],[32,6,33,6],[32,5,33,5],[32,3,33,3],[104,0,106,0],[34,0,36,0]]}
["TABLE 2 – Monitoring Points, Alarm & Trend Requirements (Applications)",{"$nulls":10},"Notes to Editor"]
["System","Point","Point Type","Trend (6)","Setpoint (1)","Alarm (4, 5)"]
[{"$nulls":5},"Description (3)","Alarm Delay","Local HMI Alarm Indication (N/A, V- visual, A- Audible) (By MSCC)","Desigo Alarm Automation (E-Email, P-Page) (7)","Trend View Definitions (7)","Priority (2)"]
["Typical HVAC Zone","Room Humidity","AI","X","i.e. 60%RH high/ 30% RH low","If humidity is <27% RH or >63% RH ",">6 hrs continuously",null,null,null,"med","Alarming and trending only required on select room applications with temperature & humidity limits required to ensure compliance with code or manufacturer (ie medical equipment) requirements","Include generic zone requirements?"]
[null,"Room Temperature","AI","X","i.e. user adjustable, 68-72°F","Alarm if room temperature is > +/-2°F of set point or space temperature is < 65°F or > 80°F","5 min",null,null,null,"med"]
["Infection Control Room Type 1 (i.e. Operating Rooms/ Delivery Rooms)","Room Temperature","AI","X","i.e. user adjustable, 62-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Via a temperature sensor located in the return branch serving room.  Room adjustable.  MSCC shall lockout thermostats based on design setpoint range."]
[null,"Room Humidity","AI","X","i.e. 60%RH high/ 30% RH low","Warning (yellow) if humidity is <30% RH or >60%RH.   Alarm (red) if humidity is <20% RH or >63% RH ",">20 min continuously",null,null,null,"high","Via humidity sensor located in the return branch serving room. Not user adjustable."]
[null,"Airchange Rate","Virtual AI","X",null,"Warning (yellow) if <22 AC's and space is OCCUPIED.  Alarm (red) if <20ACs and space is OCCUPIED","10 min",null,null,null,"high","From airflow off supply VAV box.  MSCC shall field verify room volume."]
[null,"Room Pressurization","AI","X","i.e. +0.02\" to +0.06\"WC","Alarm if <+0.01\" wc ","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Infection Control Room Types 2 or 3 (i.e. Procedure Rooms & Cardiac Cath/ Angio/ Interventional Radiology, Laser Eye Room)","Room Temperature","AI","X","i.e. user adjustable, 70-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Via a temperature sensor located in the return branch serving room.  Room adjustable.  MSCC shall lockout thermostats based on design setpoint range."]
[null,"Room Humidity","AI","X","i.e. 60%RH high/ 30% RH low","Warning (yellow) if humidity is <30% RH or >60%RH.   Alarm (red) if humidity is <20% RH or >63% RH ",">20 min continuously",null,null,null,"high","Via humidity sensor located in the return branch serving room. Not user adjustable."]
[null,"Airchange Rate","Virtual AI","X",null,"Warning (yellow) if <17 AC's and space is OCCUPIED.  Alarm (red) if <15 ACs and space is OCCUPIED","10 min",null,null,null,"high","From airflow off supply VAV box.  MSCC shall field verify room volume."]
[null,"Room Pressurization","AI","X","i.e. +0.02\" to +0.06\"WC","Alarm if <+0.01\" wc ","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Infection Control Room Type 6  (i.e. Bronchoscopy Room)","Room Temperature","AI","X","i.e. user adjustable, 68-73°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Via a temperature sensor located in the return branch serving room.  Room adjustable.  MSCC shall lockout thermostats based on design setpoint range."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs","10 min",null,null,null,"high","From airflow off supply VAV box.  MSCC shall field verify room volume."]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if >-0.01\" WC ","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es). Switch disables alarm if door is open."]
["OR Sterile Supplies Storage","Room Temperature","AI","X","i.e. user adjustable, 70-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Via a temperature sensor located in the return branch serving room.  Room adjustable.  MSCC shall lockout thermostats based on design setpoint range."]
[null,"Room Humidity","AI","X","i.e. 60%RH high/ 30% RH low","If humidity is <27% RH or >63% RH ",">6 hrs continuously",null,null,null,"med  >6hrs, high >12 hrs","Not user adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <4ACs","10 min",null,null,null,"high","From airflow off supply VAV box"]
[null,"Room Pressurization","AI","X","i.e. +0.02\" to +0.06\"WC","Alarm if ≤0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es). Switch disables alarm if door is open."]
["Airborne Infection Isolation (AII) Rooms","Room Temperature","AI","X","i.e. user adjustable, 70-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable.  MSCC shall lockout thermostats based on design setpoint range."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs & monitor in isolation mode","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressure","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if >-0.01\" wc & monitor in isolation mode","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Measured between AII room and AII Anteroom.  Provide with door switch(es).  Switch disables alarm if door is open."]
["Airborne Infection Isolation (AII) Anterooms","Airchange Rate","Virtual AI","X",null,"Alarm if <10ACs & monitor in isolation mode","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressure","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if >-0.01\" wc & monitor in isolation mode","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Measured between AII Anteroom and Corridor.  Provide with door switch(es).  Switch disables alarm if door is open."]
["Protective Environment (PE) Rooms","Room Temperature","AI","X","i.e. user adjustable, 70-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable.  MSCC shall lockout thermostats based on design setpoint range."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs & monitor in PE mode","10 min",null,null,null,"high","From airflow off supply VAV box"]
[null,"Room Pressure","AI","X","i.e. +0.02\" to +0.03\"WC","Alarm if <+0.01\" wc & monitor in PE mode","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Measured between PE room and PE Anteroom.  Provide with door switch(es).  Switch disables alarm if door is open."]
["Protective Environment (PE) Anterooms","Airchange Rate","Virtual AI","X",null,"Alarm if <10ACs & monitor in isolation mode","10 min",null,null,null,"high","From airflow off supply VAV box"]
[null,"Room Pressure","AI","X","i.e. +0.02\" to +0.03\"WC","Alarm if <+0.01\" wc & monitor in isolation mode","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Measured between PE Anteroom and Corridor.  Provide with door switch(es).  Switch disables alarm if door is open."]
["MRI Rooms","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable.  MSCC shall lockout thermostats based on design setpoint range."]
[null,"Room Humidity","AI","X","i.e. 60%RH high/ 30% RH low","If humidity is <27% RH or >63% RH ",">6 hrs continuously",null,null,null,"med  >6hrs, high >12 hrs","Not user adjustable"]
[null,"Oxygen Monitor","DO",null,"N/A","Alarm if oxygen concentration falls below 19.5% or activated via local wall switch","None",null,null,null,"life","Provide pushbutton in MRI Control Room for manually initiating purge mode.  Provide momentary pushbutton in MRI Control room for silencing alarm horn."]
[{"$nulls":11},"System to reset to normal operation when space O2 level remains above 20.5% and local reset pushbutton in MRI Control room is activated."]
["Medical Equipment Rooms (ie Cath/ EP/ IR/ MRI, etc)","Room Temperature","AI","X","i.e. 72°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Dedicated DDC temperature sensor"]
[null,"Room Humidity","AI","X","i.e. 60%RH high/ 30% RH low","If humidity is <27% RH or >63% RH ",">6 hrs continuously",null,null,null,"med  >6hrs, high >12 hrs","Not user adjustable.  Via dedicated DDC sensor"]
[null,"Leak Detection ","DI",null,"N/A","Alarm","None",null,null,null,"life","Only applicable with raised floor applications"]
["Pharmacy Workroom (including Radiopharmaceutical Workroom)","Room Temperature","AI","X","i.e. user adjustable, 68-72°F","Alarm if room temperature is <68°F or >77°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable."]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
[null,"Room Pressure","AI","X","i.e. -0.02\"WC","Alarm if ≥0\"WC","30 min (BMS), 45 sec (Local HMI)","V & A","E & P","X","high","Only applicable for Radiopharmaceutical Workrooms.  "]
["Pharmacy- Segregated Compounding Area (SCA)- Non-Hazardous (Cat 1)","Room Temperature","AI","X","i.e. user adjustable, 68-70°F","Alarm if room temperature is <60°F or >72°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable."]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
["Pharmacy- Segregated Compounding Area (SCA)- Hazardous (Cat 1)","Room Temperature","AI","X","i.e. user adjustable, 68-70°F","Alarm if room temperature is <60°F or >72°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable."]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs ","30 min","N/A","E & P","X","high","Total supply airflow into room"]
[null,"Room Pressure","AI","X","i.e. -0.02\"WC","Alarm if >-0.01\" or <-0.05\" wc","30 min (BMS), 45 sec (Local HMI)","V & A","E & P","X","high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Pharmacy Anteroom (including Radiopharmaceutical Anteroom) (Cat 2)","Room Temperature","AI","X","i.e. user adjustable, 65-66°F","Alarm if room temperature is <60°F or >68°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable."]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <30ACs ","30 min (BMS), 45 sec (Local HMI)","N/A","E & P","X","high","Total supply airflow into room, off fan filter units "]
[null,"Room Pressure","AI","X","i.e. +0.04\" to +0.06\"WC","Alarm if <+0.02\" wc","30 min (BMS), 45 sec (Local HMI)","V & A","E & P","X","high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Pharmacy- Sterile Non-Hazardous Compounding/ Beta Lactam/ Radiopharmaceutical Compounding (Cat 2)","Room Temperature","AI","X","i.e. user adjustable, 65-66°F","Alarm if room temperature is <60°F or >68°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable.\n"]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <30ACs ","30 min (BMS), 45 sec (Local HMI)","N/A","E & P","X","high","Total supply airflow into room, off fan filter units "]
[null,"Room Pressure","AI","X","i.e. +0.04\"- +0.06\"WC","Alarm if  <+0.02\" wc","30 min (BMS), 45 sec (Local HMI)","V & A","E & P","X","high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Pharmacy- Sterile Hazardous Compounding (Cat 2)","Room Temperature","AI","X","i.e. user adjustable, 65-66°F","Alarm if room temperature is <60°F or >68°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable."]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <30ACs ","30 min","N/A","E & P","X","high","Total supply airflow into room, off fan filter units "]
[null,"Room Pressure","AI","X","i.e. -0.02\"WC","Alarm if >-0.01\" or <-0.05\" wc","30 min (BMS), 45 sec (Local HMI)","V & A","E & P","X","high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Pharmacy- Hazardous Drug Storage ","Room Temperature","AI","X","i.e. user adjustable, 68-72°F","Alarm if room temperature is <68°F or >77°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable."]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs ","30 min (BMS), 45 sec (Local HMI)","N/A","E & P","X","high","Total exhaust airflow out of room "]
[null,"Room Pressure","AI","X","i.e. -0.02\"WC","Alarm if ≥0\"WC","30 min (BMS), 45 sec (Local HMI)","V & A","E & P","X","high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Pharmacy- Non-Sterile Hazardous Compounding","Room Temperature","AI","X","i.e. user adjustable, 68-72°F","Alarm if room temperature is <68°F or >77°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable."]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs ","30 min (BMS), 45 sec (Local HMI)","N/A","E & P","X","high","Total exhaust airflow out of room "]
[null,"Room Pressure","AI","X","i.e. -0.02\"WC","Alarm if >-0.01\" ","30 min (BMS), 45 sec (Local HMI)","V & A","E & P","X","high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Pharmacy- Non-Sterile Non-Hazardous Compounding","Room Temperature","AI","X","i.e. user adjustable, 68-72°F","Alarm if room temperature is <68°F or >77°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Room adjustable."]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs","Not user adjustable."]
["Pharmacy Drug Storage Rooms ","Room Temperature","AI","X","i.e. user adjustable, 68-72°F","Alarm if room temperature is <68°F or >77°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs","Coordinate spaces with drug storage with Pharmacy Department"]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs"]
["Pharmacy Product Exchange","Room Temperature","AI","X","i.e. user adjustable, 68-72°F","Alarm if room temperature is <68°F or >77°F",">6 hrs continuously","N/A","E & P","X","med  >6hrs, high >12 hrs"]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">12 hrs continuously","N/A","E & P","X","med  >12hrs, high >24 hrs"]
[null,"Room Pressurization","AI","X","i.e. +0.02\" to +0.06\"WC","Alarm if ≤0\"WC","30 min (BMS), 5 min (Local HMI)","N/A","E & P","X","high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Decontamination Rooms (CSPD)","Room Temperature","AI","X","i.e. user adjustable, 60-73°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <6ACs","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Clean Workroom (CSPD)","Room Temperature","AI","X","i.e. user adjustable, 66-73°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Room Humidity","AI","X",null,"If humidity is >60% RH ",">6 hrs continuously",null,null,null,"med  >6hrs, high >12 hrs","Not user adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <4ACs","10 min",null,null,null,"high","From airflow off supply VAV box"]
[null,"Room Pressurization","AI","X","i.e. +0.02\" to +0.06\"WC","Alarm if ≤0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Endoscope Cleaning","Airchange Rate","Virtual AI","X",null,"Alarm if <10ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Morgue & Autopsy Rooms ","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if >-0.01\" WC ","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs ","10 min",null,null,null,"high","From airflow off supply VAV box"]
["ED Decontamination Rooms ","Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC and monitor in isolation mode","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["ED Public Waiting Room","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC ","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Radiology Waiting Room","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC ","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Trauma Rooms","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <15ACs ","10 min",null,null,null,"high","From airflow off supply VAV box"]
[null,"Room Pressure","AI","X","i.e. +0.02\" to +0.03\"WC","Alarm if ≤0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Triage Rooms","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <12ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressure","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC ","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Medical/ Anesthesia Gas Storage","Airchange Rate","Virtual AI","X",null,"Alarm if <8ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Newborn Intensive Care","Room Temperature","AI","X","i.e. user adjustable, 72-78°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <6ACs ","10 min",null,null,null,"high","From airflow off supply VAV box"]
[null,"Room Pressurization","AI","X","i.e. +0.02\" to +0.06\"WC","Alarm if ≤0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Nuclear Medicine Hot Lab","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <6ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
["Nuclear Medicine Treatment Room","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <6ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
["Laboratory Work Area- bacteriology, biochemistry, cytology, general, glasswashing, histology, microbiology, nuclear medicine, pathology, serology, sterilizing","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <6ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box.  For Glasswashing Lab and Sterilizing Lab, alarm at 10 AC's"]
[null,"Room Pressurization","AI","X","i.e. -0.02\" to -0.03\"WC","Alarm if ≥0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Laboratory Work Area- media transfer","Room Temperature","AI","X","i.e. user adjustable, 68-75°F","Alarm if room temperature is > +/-3°F of set point","10 min",null,null,null,"high","Room adjustable"]
[null,"Airchange Rate","Virtual AI","X",null,"Alarm if <4ACs ","10 min",null,null,null,"high","From airflow off exhaust VAV box"]
[null,"Room Pressurization","AI","X","i.e. +0.02\" to +0.06\"WC","Alarm if ≤0\"WC","30 min (BMS), 5 min (Local HMI)",null,null,null,"high","Provide with door switch(es).  Switch disables alarm if door is open."]
["Telecommunication Rooms (see SBA-C-H)","Space Temperature","AI","X","i.e. user adjustable, 68-72°F","Alarm if room temperature is > 80°F ",{"$nulls":4},"high","Room adjustable"]
[null,"Leak Detection (Floor)","DI",null,"N/A","Alarm","None",null,null,null,"high","Only required when a possible source of water leak exists in the room (i.e. water piping, FCU)."]
["Substation Rooms, Elevator Machine Rooms, Electrical Rooms","Space Temperature","AI","X","i.e. 65°F","Alarm if room temperature is <50°F or >105°F ",{"$nulls":4},"high","For naturally ventilated spaces"]
[{"$nulls":5},"Alarm if room temperature is <50°F or >85°F ",{"$nulls":4},"high","For mechanically cooled spaces"]
[null,"Leak Detection","DI",null,"N/A","Alarm","None",null,null,null,"high","Only required when a possible source of water leak exists in the room (i.e. water piping, FCU)."]
["Generator Room","Space Temperature","AI","X","i.e. 65°F","Alarm if room temperature is <50°F or >105°F ",{"$nulls":4},"high"]
[null,"Intake & Exhaust Dampers","DI",null,"N/A","If damper position not open with generator running","10 sec",null,null,null,"high"]
["Computer/ Server Rooms","Room Temperature (several locations)","AI","X","i.e. 68-72°F","Alarm if room temperature is > +/-3°F of set point or space temperature is  >77°F",{"$nulls":4},"high","Typically several locations in the room"]
[null,"Room Relative Humidity","AI","X",null,"If humidity is >63% RH ",">6 hrs continuously",null,null,null,"high"]
[null,"Raised Floor Temperature","AI","X","i.e. 60°F","Alarm if room temperature is > +/-2°F of set point ",{"$nulls":4},"high","Typically several locations in the room"]
[null,"Raised Floor Static Pressure","AI","X","i.e. 1.25\" WC","If > +/-0.5\"WC of set point",{"$nulls":4},"high","Typical each transmitter"]
["NOTES:"]
["1. Setpoints are project specific, AE of record to edit setpoints in italics to reflect design"]
["2. Alarm Types: life = Life Safety (0-31 Alarm Priority). high = High Priority (64-95 Alarm Priority). med = Medium Priority (96-127 Alarm Priority). low = Low Priority (128-191 Alarm Priority)"]
["3. All alarm values shall be adjustable thru the frontend graphic"]
["4. Trend Types: COV= Change of Value.   INT= Interval (Interval trends set to time)"]
["4. Configure alarms as indicated.  Alarms in the local DDC shall be configured by the MSCC (Mech System Controls Contractor).  Alarms in the Desigo frontend shall be configured by the SI (Systems Integrator).  "]
["4. MSCC shall configure alarms as indicated in the local DDC panel.  "]
["5. Alarm requirements based on compliance with ASHRAE 170, 2017 & USP 795/ 797/ 800/ 824"]
["6. Trends shall be configured in the local DDC panel by the MSCC."]
["7. Trend View Definitions and Desigo Alarm Automation shall be setup by the Systems Integrator (SI)"]
["8.  MM's Desigo front-end operates on (3) servers.  System 1 (instance #9997) encompasses the C&W facility.  System #2 (instance #9998) encompasses Power Monitoring and Area 5 (offsite) buildings.  System 3 (instance #9996) encompasses all remaining facilities on the hill campus (UH, UHS, CVC, CC, THC)."]
[]
["NOTES TO EDITOR:"]
["A. Table is meant to reflect the MINIMUM standardized points, alarms and trends reporting back to UMH’s BMS.  Since control strategies and controller technologies vary greatly form project to project, UMH recognizes that different point and/ or alarm/ trend requirements may be necessary.  Consult with the appropriate UMH FPD Mechanical Engineer."]
["B. For room applications not listed in Table 2, generally trends and alarms are not required.  A/E shall exercise judgement on requiring alarms/ trends in non-compliance applications where there is significant risk/ financial implications with HVAC failures (ie consider temperature/ humidity alarming/ trending in medical equipment applications to ensure environmental requirements of the equipment are being met)."]
["C. Alarms should be configured in the local DDC panel for points that are rarely changed by Systems Monitoring.  Alarms should be configured in the Desigo BMS for points that are frequently overridden for operational reasons.  AE shall review alarm configuration requirements with FPD engineer. \t\t\t\t\t\t\t\t\t\t"]