{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Elec Table 1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Elec Table 1","index":0,"n_rows":107,"n_cols":10,"rows_kept":107,"cut":false,"hidden":false,"merged":[[1,0,2,0],[1,1,2,1],[1,2,2,2],[64,0,83,0],[0,0,0,9],[1,9,2,9],[1,3,1,5],[1,6,1,8],[4,0,18,0],[84,0,95,0],[105,0,105,9],[106,0,106,9],[3,0,3,9],[33,0,33,9],[63,0,63,9],[102,0,102,9],[103,0,103,9],[104,0,104,9],[35,0,62,0],[96,0,100,0],[19,0,32,0]]}
["TABLE 1 – Monitoring Points, Alarm & Trend Requirements (Power Monitoring)"]
["System","Point","Point Type","Trending Parameters",null,null,"Alarm",null,null,"Notes"]
[null,null,null,"Trend","Type (4)","Time of Trend","Description (3)","Alarm Delay","Priority (2)"]
["Electrical Power Equipment"]
["Power Meter","RMS amperes (By Phase)","AI","X","INT","10 min"]
[null,"RMS volts (Phase-Phase average)","AI","X","INT","10 min"]
[null,"kW (each Phase)","AV","X","INT","10 min"]
[null,"kW Avg","AV","X","INT","10 min"]
[null,"kVA (each Phase)","AV","X","INT","10 min"]
[null,"KVAR (each Phase)","AV","X","INT","10 min"]
[null,"kWh","AV","X","INT","10 min"]
[null,"Power Factor","AV","X","INT","10 min"]
[null,"Frequency (each Phase)","AV","X","INT","10 min"]
[null,"Voltage imbalance Alarm ","AV","X","INT","10 min","Voltage Imbalance",null,"low","Imbalance > 30%"]
[null,"Voltage Sag or Swell Alarm","DI","X","COV","N/A","Voltage Sag or Swell",null,"low"]
[null,"Frequency imbalance Alarm","DI","X","COV","N/A","Frequency Imbalance",null,"low","Imbalance > 5 Hz"]
[null,"Waveform Capture Alarm ","DI","X","COV","N/A","Waveform Captured",null,"low","*Only on Advanced Meters."]
[null,"Event Alarm","DI","X","COV","N/A","Event Alarm",null,"low","*Only on Advanced Meters."]
[null,"THD Alarm ","DI","X","COV","N/A","THD Alarm",null,"low","*Only on Advanced Meters."]
["Trip Unit","Main Breaker Status","AI","X","INT","10 min","Main Breaker Status",null,null,"Racked, tripped, Open, closed"]
[null,"Main Breaker Trip","DI","X","COV","N/A","Main Breaker  Trip",null,"life"]
[null,"Breaker Status (all circuits)","AI","X","INT","10 min","Breaker Status",null,null,"Racked, tripped, Open, closed"]
[null,"Breaker Trip (all circuits)","DI","X","COV","N/A","Breaker Trip",null,"high"]
[null,"RMS amperes Total (all Circuits)","AI","X","INT","10 min"]
[null,"RMS volts (Phase-Phase average) - PDU only","AI","X","INT","10 min",null,null,null,"Data Center"]
[null,"kW Total - PDU main ","AI","X","INT","10 min",null,null,null,"Data Center"]
[null,"kW Total (all circuits) ","AI","X","INT","10 min"]
[null,"kVA Total (all Circuits)","AI","X","INT","10 min"]
[null,"kWh (Total for PDU)","AI","X","INT","10 min"]
[null,"Power Factor","AI","X","INT","10 min"]
[null,"Voltage imbalance Alarm ","AV","X","INT","10 min","Voltage Imbalance",null,"low","Imbalance > 30%"]
[null,"Voltage Sag or Swell Alarm","AV","X","INT","10 min","Voltage Sag or Swell",null,"low"]
[null,"Power Factor - PDU only","AI","X","INT","10 min",null,null,null,"Data Center"]
["Misc. Electrical Equipment"]
["Lighting Control (If Necessary)","Enable/ Disable","DO","X","COV","N/A","Lighting Control Disabled",null,"low"]
["UPS ","UPS Com Module Failure Alarm","AI","X","INT","10 min","Comm Alarm",null,"low"]
[null,"Current (per phase, input, output & three-phase)","AI","X","INT","10 min","Current above 65% of available",null,"low"]
[null,"Voltage (per phase, input, output & three-phase)","AI","X","INT","10 min","Voltage Imbalance",null,"low","Imbalance > 30%"]
[null,"Bypass Current (per phase, input, output & three-phase)","AI","X","INT","10 min","UPS in Bypass",null,"low"]
[null,"Bypass Voltage (per phase, input, output & three-phase)","AI","X","INT","10 min","UPS in Bypass",null,"low"]
[null,"Frequency (Input & output)","AI","X","INT","10 min","General alarm if out of balance",null,"low"]
[null,"kVA (Input & output)","AI","X","INT","10 min"]
[null,"UPS Battery Current","AI","X","INT","10 min","General alarm",null,"low"]
[null,"UPS Battery Voltage","AI","X","INT","10 min","Alarm if less than 90% of setpoint",null,"high","Setpoint to be determined"]
[null,"Estimated Minutes Remaining","AI","X","INT","10 min","Alarm if less than 90% of setpoint",null,"high","Setpoint to be determined"]
[null,"Estimated Charge Remaining","AI","X","INT","10 min"]
[null,"Flywheel Frequency","AI","X","INT","10 min","Flywheel Frequency Low",null,"high","> 55 Hz"]
[null,"Flywheel Capacity (%)","AI","X","INT","10 min"]
[null,"Flywheel Speed","AI","X","INT","10 min"]
[null,"Flywheel Voltage","AI","X","INT","10 min","Flywheel Low Voltage",null,"high","< 460V"]
[null,"String Voltage","AI","X","INT","10 min","String Voltage Low",null,"high","< 90% of Setpoint"]
[null,"String Current","AI","X","INT","10 min"]
[null,"String Average Cell Voltage","AI","X","INT","10 min","String Avg Cell Voltage Low",null,"high","< 90% of setpoint"]
[null,"String Float Current","AI","X","INT","10 min"]
[null,"Breaker Status (Input, Output, External & Internal)","AI","X","INT","10 min"]
[null,"Breaker Trip (Input, Output, External & Internal)","DI","X","COV","N/A","Breaker Trip",null,"life"]
[null,"UPS Trouble","DI","X","COV","N/A","General alarm",null,"life"]
[null,"UPS on Battery","DI","X","COV","N/A",null,null,"life"]
[null,"UPS Failure","DI","X","COV","N/A",null,null,"life"]
[null,"UPS on Bypass","DI","X","COV","N/A",null,null,"life"]
[null,"UPS on Inverter","DI","X","COV","N/A",null,null,"life"]
[null,"UPS Battery Disconnect Status","DI","X","COV","N/A","General alarm",null,"life"]
[null,"UPS Com Module Failure Alarm","DI","X","COV","N/A","Comm Alarm",null,"life"]
["Emergency Power Equipment"]
["Emergency Generator","Engine Comm Module Failure ","DI","X","COV","N/A","Comm Alarm",null,"life","General alarm from generator control panel"]
[null,"Gen Run / Stop","AI","X","INT","10 min",null,null,null,"Status from generator control panel"]
[null,"Current (per phase, three-phase)","AI","X","INT","10 min",null,null,null,"From Meter"]
[null,"Voltage (per phase, normal, emergency & three-phase)","AI","X","INT","10 min",null,null,null,"From Meter"]
[null,"kW Total (all circuits) ","AI","X","INT","10 min",null,null,null,"From Meter"]
[null,"kVA Total (all Circuits)","AI","X","INT","10 min",null,null,null,"From Meter"]
[null,"kWh (Total)","AI","X","INT","10 min",null,null,null,"From Meter"]
[null,"Power Factor","AI","X","INT","10 min",null,null,null,"From Meter"]
[null,"Crank Attempts","AI","X","INT","10 min",null,null,null,"Status from generator control panel"]
[null,"Gen Not in Auto","DI","X","COV","N/A",null,null,"high","Status from generator control panel"]
[null,"Successful Starts","AI","X","INT","10 min",null,null,null,"Status from generator control panel"]
[null,"Engine Cooling Temperature","AI","X","INT","10 min","Engine High Cooling Temperature",null,"life","Status from generator control panel"]
[null,"Engine Oil Temperature","AI","X","INT","10 min","Engine High Oil Temperature",null,"life","Status from generator control panel"]
[null,"Engine Oil Pressure","AI","X","INT","10 min","Engine High Oil Pressure",null,"life","Status from generator control panel"]
[null,"Operating Hours","AI","X","INT","10 min",null,null,null,"Status from generator control panel"]
[null,"Fuel Pressure","AI","X","INT","10 min",null,null,null,"Status from generator control panel"]
[null,"Gen Trouble","DI","X","COV","N/A",null,null,"life","Status from generator control panel"]
[null,"Gen Fail","DI","X","COV","N/A",null,null,"life","Status from generator control panel"]
[null,"Gen Battery Charger Fail","DI","X","COV","N/A",null,null,"high","Status from generator control panel"]
[null,"Gen Breaker Open","DI","X","COV","N/A",null,null,null,"Status from generator control panel"]
["Automatic Transfer Switch","Transfer Switch Controller Comm Failure Alarm","DI","X","INT","10 min","Signifies emergency power is active",null,"life","Connect in series each “on generator power” auxiliary contact in each ATS to a single point in a DDC panel to notify the BMS if any ATS transfers to generator power"]
[null,"Switch in Normal Position","DI","X","COV","N/A"]
[null,"Current (per phase, three-phase)","AI","X","INT","10 min","Current > 65%",null,"high"]
[null,"Voltage (per phase, normal, emergency & three-phase)","AI","X","INT","10 min"]
[null,"kW Total (all circuits) ","AI","X","INT","10 min"]
[null,"kVA Total (all Circuits)","AI","X","INT","10 min"]
[null,"kWh (Total)","AI","X","INT","10 min"]
[null,"Switch in Emergency Position","DI","X","COV","N/A",null,null,"life"]
[null,"Switch Not In Auto","DI","X","COV","N/A",null,null,"high"]
[null,"Emergency Source Available","DI","X","COV","N/A"]
[null,"Normal Source Availble","DI","X","COV","N/A"]
[null,"Switch in Bypass","DI","X","COV","N/A"]
["Fuel Oil Systems","Pump Status","DI","X","COV","N/A",null,null,null,"From pump controller"]
[null,"Alarm","DI","X","COV","N/A","General alarm",null,"life","General alarm from pump controller"]
[null,"Fuel Quantity","AI","X","INT","10 min","Alarm upon loss of fuel below 50% (warning) and 20% (alarm)",null,"life","Fuel quantity in main storage tank"]
[null,"Day Tank Fuel Level- Critical Low ","DI","X","COV","N/A",null,null,"life","From pump controller"]
[null,"Day Tank Fuel Level- Critical High ","DI","X","COV","N/A",null,null,"life","From pump controller"]
["Fuel Oil Leak Detection","Alarm","DI","X","COV","N/A","General alarm",null,"high","General alarm from leak detection panel"]
["NOTES:"]
["1. Table is meant to reflect the MINIMUM standardized points reporting back to UMH’s front-end graphic interface and should be used as a GUIDE during the design phase.  Since control strategies and controller technologies vary greatly form project to project, UMH recognizes that different point and/ or alarm capabilities may be necessary.  Consult the appropriate UMH FPD Electrical Engineer prior to finalizing any control design."]
["2. Alarm Types: life = Life Safety (0-31 Alarm Priority). high = High Priority (64-95 Alarm Priority). med = Medium Priority (96-127 Alarm Priority). low = Low Priority (128-191 Alarm Priority)"]
["3. All Alarm setpoints & thresholds shall be adjustable thru the frontend graphic"]
["4. Trend Types: COV= Change of Value.   INT= Interval.   (Interval trends set to time)"]